## Annex B - Offer and BoQ
ANNEX B - Financial Offer Form and Bill of Quantities - Labour-Based Unit Rates
HOW TO COMPLETE: Enter a unit rate (ETB, excluding VAT) for EVERY item in the yellow cells of column E. Amounts and totals calculate automatically. This is a LABOUR-BASED contract: rates cover labour, supervision, tools, test instruments, PPE, transport, accommodation, overheads and the minor items in Annex A, Section 4. DO NOT price any material listed in Annex F – UNHCR supplies these. The only material priced by the contractor is the additional 100 m of duct in item B3. Items E1–E5 are provisional (paid only if instructed after the survey) but must be priced; their quantities are used for price comparison. Example: a unit rate of 900 in E for item B1 gives 250 × 900 = 225,000 ETB in F.
Item | Description of work | Unit | Qty | Unit rate (ETB, excl. VAT) | Amount (ETB) | Materials (Annex F codes) | Measurement and notes
A. PRELIMINARIES AND SURVEY
A1 | Mobilisation to Nyinyang, site establishment, site store, and demobilisation | Lot | 1 |  | 0 | — | Includes transport and accommodation of personnel, tools and instruments.
A2 | Site verification, electrical survey of existing buildings, survey report and joint material count | Lot | 1 |  | 0 | — | Annex A, 5.1. Survey report within 5 calendar days of commencement.
B. UNDERGROUND WORKS
B1 | Cable trench: excavation, bedding, warning tape, backfill, compaction and reinstatement | m | 250 |  | 0 | Warning tape Q59411. Bedding sand and backfill: contractor | Measured once per metre of completed trench, whatever the number of cables. Approx. 167 m power + 30 m earth + 25 m lighting crossings, rounded.
B2 | Underground duct 50 mm: lay, joint and seal ends | m | 250 |  | 0 | Q30057 | Each duct measured separately. 150 m from UNHCR stock (Annex F, Q30057) and 100 m supplied by the contractor (B3).
B3 | Supply of additional 50 mm corrugated underground duct (same type as Q30057), delivered to the Nyinyang site | m | 100 |  | 0 | Contractor-supplied (not in Annex F) | Supply only; installation is paid under B2. This is the only material the contractor supplies and prices in this BoQ.
C. SITE DISTRIBUTION AND EARTHING
C1 | Field power cables: lay, fix, terminate both ends and label | m | 500 |  | 0 | Q51833, Q51842, Q12931 | Measured along each completed cable run. Cable types and sizes as on drawing E.1.
C2 | Security-lighting cables: lay, fix, connect and label | m | 500 |  | 0 | Q51822, Q51682, Q51408 | Measured along each completed cable run.
C3 | Site distribution boards: install, connect and label (5 × 63 A Garo with stands, 1 × 32 A El-Björn, 1 × 160 A switch enclosure) | No. | 7 |  | 0 | Q30096, Q30091, Q30066 | Per board, including incoming and outgoing terminations and tests. 250 A main board excluded.
C4 | Earthing conductor Cu 25 mm²: lay in trench, connect, including bonding connections | m | 200 |  | 0 | Q30060, Q34103, Q51696 | Measured along the completed conductor route.
C5 | Earth electrode with test pit and cover (E1–E6), including resistance test | No. | 6 |  | 0 | Q30090, Q31390–Q31392. Pit and cover: contractor | Per completed electrode. Depth as confirmed by the engineer.
D. BUILDINGS, LIGHTING AND EQUIPMENT CONNECTIONS
D1 | New prefab: complete electrical installation of one module, including CEE 32 A inlet and onward outlet, smoke alarms and tests | No. | 12 |  | 0 | Prefab kits; Q59719, Q59720, Q12142, Q14541 | Per module (8 accommodation + 4 hygiene). Timers and fans are priced only in D6 and D7.
D2 | Security floodlight 72 W: mount, connect, aim and test | No. | 24 |  | 0 | Q51831 | Per fitting. Cables in C2. Poles only where shown on E.1.
D3 | Outdoor wall luminaire: mount, connect and test | No. | 14 |  | 0 | Q51716 | Per fitting.
D4 | Industrial LED luminaire 36 W in the five named rooms (Annex A, 5.6) | No. | 5 |  | 0 | Q51688 | Per fitting, including local wiring.
D5 | Electrical supply point for an AC unit, with isolator and connection | No. | 4 |  | 0 | Annex F accessories | Old and new guardhouse, technical container, office ICT room. Mechanical installation by others.
D6 | AC timer: install, wire and test | No. | 20 |  | 0 | Q51347 | Per timer, wherever installed (including new prefabs).
D7 | Ceiling fan: install with structural support and control, and test | No. | 6 |  | 0 | Q17757 | Per fan, wherever installed.
D8 | Water pump: dedicated circuit with weatherproof switched socket | No. | 1 |  | 0 | Annex F cable and socket | Mechanical pump and pipework by others.
D9 | Incinerator: dedicated circuit with weatherproof switched socket | No. | 1 |  | 0 | Annex F cable and socket | Check nameplate (E.1: 220 V, 1.55 kW, 10 A).
E. PROVISIONAL ITEMS – EXISTING BUILDINGS (paid only if instructed in writing after the survey)
E1 | Additional luminaire (industrial LED or ceiling ALU): install, connect and test | No. | 40 |  | 0 | Q51688, Q51714, Q51715 | Provisional. Stock available: 43 industrial LED + 20 ceiling ALU.
E2 | Replacement distribution board 32 A three-phase, including transfer of existing circuits | No. | 10 |  | 0 | Q30091, Q59459 (or Hager components Q51614, Q51622, Q51616, Q51615, Q51706) | Provisional. Per complete board. Stock after C3: 11 El-Björn 32 A boards (9 × Q30091 + 2 × Q59459), which covers the 10 provisional replacements.
E3 | CEE 32 A three-phase inlet or outlet: install or replace | No. | 16 |  | 0 | Q59719, Q59720 | Provisional. Stock after D1: 8 inlets + 8 outlets.
E4 | Internal wiring replacement, including trunking and junction boxes | m | 100 |  | 0 | Q51822, Q51686, Q51687, Q59722 | Provisional. Per metre of completed cable run.
E5 | Switch or socket assembly: install or replace | No. | 40 |  | 0 | Q51491, Q51707, Q51828, Q51406 | Provisional. A multi-gang unit counts as one.
F. TESTING, COMMISSIONING AND HANDOVER
F1 | Testing and commissioning of the whole installation in both compounds, with signed test sheets | Lot | 1 |  | 0 | — | Annex E, Section 11. Includes smoke-alarm checks outside the prefabs.
F2 | As-built drawings, O&M dossier, training of nominated staff and final material reconciliation | Lot | 1 |  | 0 | — | Annex A, 5.10; Annex E, Section 12.
Subtotal section A |  |  |  |  | 0 | Notes: 1. Quantities are measured on completion; payment is for completed, accepted quantities at these unit rates. 2. Section E quantities are provisional; final quantities follow the approved survey (Annex A, 5.9). 3. Ducts: 250 m are needed; UNHCR supplies 150 m and the contractor supplies 100 m under B3. Any other material shortfall is supplied by UNHCR; do not price it. 4. VAT rate 15% (Ethiopian standard rate); enter the reason in the Bid Submission Form if VAT does not apply.
Subtotal section B |  |  |  |  | 0
Subtotal section C |  |  |  |  | 0
Subtotal section D |  |  |  |  | 0
Subtotal section E |  |  |  |  | 0
Subtotal section F |  |  |  |  | 0
TOTAL EXCLUDING VAT (ETB) |  |  |  |  | 0
VAT (15 %) |  |  |  |  | 0
TOTAL INCLUDING VAT (ETB) – carry to the Bid Submission Form |  |  |  |  | 0
BIDDER'S CONFIRMATION
Our unit rates are for labour and services only. We have NOT priced any material listed in Annex F. | [5 empty] | Yes ☐ No ☐
We will complete the works within 20 calendar days of the agreed commencement date. | [5 empty] | Yes ☐ No ☐
Our offer is valid for at least 60 days from the bid deadline. | [5 empty] | Yes ☐ No ☐
We accept UNHCR payment terms: net 20 days after acceptance of the works and receipt of a correct invoice. | [5 empty] | Yes ☐ No ☐
Company name
Name and title of authorised person
Signature
Company stamp and date
Legend: yellow cells = to be completed by the bidder; blue figures = quantities and rates set by UNHCR; all other figures are calculated.